Ongoing site investigations have found made ground in excess of 5.0m depth on the MVT site. Therefore, soakaways will not be possible. The drainage strategy will therefore comprise a Polystorm type attenuation tank and hydrobrake manhole restricting SW discharge to 5  l/s  into the site wide drainage system, as shown on the drainage strategy drawing ref 10-5637-500c.
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